## Sheet1
submersible pump with motor for Boreholes with 12 – 14 inch casing diameter
Item No. | item description | Casing inner diameter (inch) | Q l/s or (m3/h) | Head(m) | Efficency of pump | efficencey of motor | Water temp.in °C | Pump position | The pump outlet size & connection type | Minimum clearance b/n casing and pump or flange (mm) | Motor Starter Type
[5 empty] | % | % |  | (m)
1 | submersible pump with motor | 14” | 70 (252) | 250 | 70 | 80 | 50 | 154 | 4” threaded | 25 | Y/D
2 | submersible pump with motor | 14” | 50 (180) | 284 | 70 | 80 | 50 | 130 | 4” threaded | 25 | Y/D
3 | submersible pump with motor | 14” | 20(72) | 250 | 70 | 80 | 50 | 165 | 4” threaded | 25 | Y/D
4 | submersible pump with motor | 12” | 50 (180) | 284 | 70 | 80 | 50 | 180 | 4” threaded | 25 | Y/D
General Technical Requirements of the pumps
item.No. | Item description | Technical Requirements
1 | Submersible Borehole Pump for potable water | The pump shall be designed and constructed to be suitable for pumping of potable water and shall be designed to give the specified output against all loses including those relating to pump station pipe work and valves. The pump to be supplied shall have the pump efficiency as specified in particular requirement and reliability at a given duty point. The whole pumping unit shall be capable of withstanding, without detriment, reverse rotation to a speed that would occur if the pump were to stop when the differential head was at a maximum and the delivery and/or non-return valve failed to close. The material and the pump construction will be suitable for the ground water quality characterized mainly by:  Sand content to 50 g/m3  Low PH, minimum 5  High co2 content up to 100g/l The submersible pumps & related accessories shall operate in and around the Addis Ababa city at altitude around 2400 m.a.s.l. and the average maximum ambient temperature is 280c and the average minimum temperature is 70C.
2 | Pump Casing | The pump design shall ensure that alignment is maintained between the various assemblies by recesses, spigots and dowels and shall be that all components liable to wear can be replaced. Components shall be permanently marked with the manufacturer’s number and where dowels are not used, permanently marked for correct assembly. The pump casing shall have replaceable wear rings. The casing of the pump shall be of a suitable grade of close grained cast iron to BS EN 1561:1997(specification for flake graphite cast iron) grade 220 or ductile cast iron or nickel iron or stainless steel and have flanged or traded connection to match the specified pipe work
3 | Impellers | The impellers and guide vane shall be of suitable material preferably cast in high-grade zinc free bronze or stainless steel, accurately machined and smoothly finished to minimize hydraulic losses. The pump shall be equipped with wear rings of renewable/replaceable type, made of zinc free bronze, stainless steel, metal reinforced rubber and having larger bearing surface. The rotating element shall be statically and dynamically balanced before final assembly
4 | Pump Shaft | The pump shaft shall be of high tensile strength stainless steel or chrome steel adequately sized, with good fatigue, shock load and corrosion resistant. The duty speed range shall be well below the first critical speed of the shaft. Where a change in diameter of the shaft occurs the shoulder shall have a radius or undercut to appropriate BS to reduce stress concentration. The shaft shall be complete with easily renewable/replaceable stainless steel or bronze protecting sleeves at glands and bearings.
5 | Bearings | Bearings shall be rated to ensure cool running and meet the load factors specified. The bearings shall be water lubricated. The motor thrust bearings should be capable to carry thrust load corresponding to the maximum head operating with rotation in either direction. Bearing shall be positively retained within the pump body to prevent the possibility of the bearing rotating; a press fit alone shall not be acceptable. The pump shall be fitted with a suction case of a material suitable for the liquid being pumped and shall be provided with long bearings to stabilize the shaft and motor shaft and to avoid radial thrust on the motor bearing. A screen shall be incorporated having a minimum open area of four times the eye of the impeller.
6 | Submersible Electric Motor | The motor shall be suitable for three phase 380V, 50 Hz power supply and shall comply in all aspects with the relevant parts of BS 4999(general requirements for rotating electrical machines) and BS 5000 (Rotating electrical machines of particular types or for particular types) or equivalent, and shall be designed to run at high power factor and efficiency at the prescribed plant duty. The starting (locked rotor) current of the motor shall not exceed 6 times the full load operating current. Motor starting torque shall be at least 120% of the pump torque requirements throughout the starting sequence. Motors shall be capable of running backwards at rated speeds under backflow conditions without damage to the motor. The motor shall be capable of continuous operation under water. The protection index for motors shall be IP 68. The motor shall be installed vertically and rigidly coupled to the multistage submersible pump such that both the pump and motor are completely flooded and stator should be rewindable.
specify the technical details of listed below
Item.No. | Item description | Rating/technical specification | Remark
1 | Pump
1.1 | Manufacturer
1.2 | Country of origin
1.3 | Model designation
1.4 | Pump Serial No.
1.4.1 | Required pump head, HR (m) , (not to be altered)
1.4.2 | Offered pump flow (m3/h) for the required pump head
1.5 | Rated flow (m3/hr)
1.6 | Rated head (m)
1.7 | Efficiency at rated flow (%)
1.8 | Power absorbed at rated flow (KW)
1.9 | Power absorbed at duty point ( KW)
1.1 | Efficiency at duty point (%)
1.11 | Power absorbed at duty point ( KW)
1.12 | Pump out let size (mm)
1.13 | Pump outlet connection Type ( Threaded or Flanged )
1.14 | Material of shaft
1.15 | Material of casing
1.16 | Material of impeller
1.17 | Material of non-return valve
1.18 | Pump diameter over the cable (mm)
1.19 | Allowable maximum sand particles content in water
1.2 | Recommended borehole casing diameter (mm)
1.21 | Pipe clamp thickness (mm)
2 | Electric Motor
2.1 | Manufacturer
2.2 | Country of origin
2.3 | Model designation
2.4 | Motor serial No.
2.5 | Submersible motor type (whether rewind able or replaceable type)
2.6 | Actual speed at full load (RPM) | 3000 RPM+5%
2.7 | Rated Power (KW)
2.8 | Supply voltage (V)
2.9 | No load current (A)
2.1 | Full load current (A)
2.11 | Starting current (A)
2.12 | Efficiency at full load (%)
2.13 | Efficiency at duty point (%)
2.14 | Efficiency at 3/4 load (%)
2.15 | Efficiency at 1/2 load (%)
2.16 | Material of motor body
2.17 | Stator winding conductor type & ratings
2.18 | Motor winding temperature sensor type
2.19 | Insulation class
2.2 | Protection Index
2.21 | Motor Diameter (mm)
2.22 | Cooling water flow across the motor surface ( m/s )
2.23 | Recommended Space requirement between casing and motor inside the borehole